## Slide 1
Start Time
Capture Name
Sample
Sep 14, 2020 - 3:58 PM
Capture Length
56 minutes
Audit Report

## Slide 2: Overview
BACPro™ provides unrestricted live monitoring, analysis of offline captures, and comprehensive reporting. Every day, millions of BACnet® messages are sent over your network to the devices that comprise your building control system. Adding to the complexity, the network is often shared by devices from different vendors that do not always work seamlessly together.
When problems occur, it often takes a BACnet expert hours or days to review network capture files, understand the causes, and then pinpoint the problematic device or workstation. BACPro cuts through the complexity and saves you time by providing non-stop analysis of every BACnet packet on your network—and then highlights the problem areas.

## Slide 3: Network Analysis
BACPro Expert Network Analysis

## Slide 4: Network Health Scores
Chart: 
| Connectivity | Performance | Integrity
Series 1 | 0.97131 | 0.74321 | 0.031833 | #N/A
Connectivity
A measure of all devices that are communicating correctly. This means they answer requests and answer I-am. Only devices that have talked on the network at least once are counted. If there is a who-is to a device that has never talked on the network, it is not counted since this could just be a configuration error.
Performance
A rating based on how fast devices answer requests. The faster a device answers, the better the score. To get the highest score, IP devices must answer within 200ms on average, and MSTP devices must answer within 400ms.
Integrity
A score that starts at 100% and decreases in accordance with the severity of each anomaly discovered on the network. Fix the most severe anomalies first. Examples of integrity issues are misconfigured BBMDs, duplicate addresses, duplicate routers, excessive broadcasts, and router errors.
Critical
Overall Capture Health

## Slide 5: Network Traffic
Chart: 
| Read Property | Who-Is | I-Am | COV Notification | Private Transfer | Read Property Multiple | Who-Has | Read Range | Event Notification | Subscribe COV | Message Notification | I-Have | All Other | Time Sync | Write Property
NetworkTraffic | 190776 | 145924 | 68941 | 23863 | 21082 | 14475 | 14038 | 6401 | 2413 | 2160 | 1046 | 448 | 224 | 132 | 40
38.78% 190776
29.66% 145924
14.01% 68941
4.85% 23863
4.29% 21082
2.94% 14475
2.85% 14038
1.3% 6401
0.49% 2413
0.44% 2160
0.21% 1046
0.09% 448
0.05% 224
0.03% 132
0.01% 40
Discovered Networks:
107
Discovered Devices:
1065

## Slide 6
Critical Anomalies
Duplicate Router To Network

## Slide 7
Duplicate Router To Network
-- Most recent 10
Two routers that answer I-am Router to Network for the same network number to a single device is a severe configuration error. A device should only know one router per network.
Time | Network | Router 1 | Router 2
9/14/2020 4:05:26 PM | 101 | 10.161.52.31 | 10.160.64.231

## Slide 8
High Anomalies
Device Failed
Device Return
Duplicate BBMD
Duplicate Instance
Excessive Who-Is

## Slide 9
Device Failed
-- Most recent 10
A device failure has been detected. It is not answering a Who-Is or poll for master but was communicating previously.
Time | Instance | MAC Address | Type | Comment
9/14/2020 4:51:52 PM | 8205 | Net=8200 - 5 - 47808 | Failure | 
9/14/2020 4:51:49 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:49:26 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:46:50 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:46:42 PM | 7162 | Net=7100 - 62 - 47808 | Failure | 
9/14/2020 4:44:26 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:42:05 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:39:42 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:34:45 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Failure | 
9/14/2020 4:33:02 PM | 7160 | Net=7100 - 60 - 47808 | Failure | 

## Slide 10
Device Return
-- Most recent 10
A device has returned from failure.
Time | Instance | MAC Address | Type | Comment
9/14/2020 4:53:52 PM | 8205 | Net=8200 - 5 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:53:25 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:51:29 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:50:26 PM | 7162 | Net=7100 - 62 - 47808 | Return | Length of failure: 3 minutes.
9/14/2020 4:49:25 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:46:24 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:43:39 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:41:37 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 2 minutes.
9/14/2020 4:38:06 PM | 70307 | Net=0 - 10.160.32.75 - 47808 | Return | Length of failure: 3 minutes.
9/14/2020 4:35:52 PM | 9209 | Net=9200 - 9 - 47808 | Return | Length of failure: 3 minutes.

## Slide 11
Duplicate BBMD
-- Most recent 10
Duplicates cause excessive traffic on the network. Make sure there is only 1 BBMD per network segment.
Time | Address 1 | Address 2
9/14/2020 4:05:26 PM | 10.110.84.111 | 10.110.84.112

## Slide 12
Duplicate Instance
-- Most recent 10
Two different devices are reporting the same instance number to a device. Duplicate device instances with different MAC addresses is a configuration error. A workstation cannot communicate correctly with these devices. If this is the workstation instance with multiple connections this error can be supressed.
Time | Instance | MAC Address 1 | MAC Address 2
9/14/2020 3:59:28 PM | 101218 | Net=0 - 10.160.27.98 - 47808 | Net=35679 - 0.0.0.1.139.98 - 47808

## Slide 13
Excessive Who-Is
-- Most recent 10
Who-Is traffic is excessive. Who-is calls put a burden on every device that must process them.
Time | Comment
9/14/2020 4:02:55 PM | Overall amount of Who-is traffic is too high.

## Slide 14
Medium Anomalies
Excessive COVs
Excessive Events
High Broadcast Rate
Incorrect Password Error
Overloaded/Restarting Device
Preempted By Higher Priority Task
Reject Message to Network
Timeout Error
Unknown Object
Unresponsive Device

## Slide 15
Excessive COVs
-- Most recent 10
High COV traffic puts a burden on workstations or devices that must process each message. Try adjusting COV limits. Those in this list have more than 30 in one minute.
Time | Source Instance | Object ID | Property | Source Address | Destination Address
9/14/2020 4:52:57 PM | 710012 | AnalogValue - 5 | present-value | Net=11001 - 2 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 4:01:55 PM | 70104 | AnalogInput - 0 | present-value | Net=0 - 10.164.11.234 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 4:00:55 PM | 70104 | AnalogInput - 1 | present-value | Net=0 - 10.164.11.234 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 4:00:55 PM | 70104 | AnalogValue - 3 | present-value | Net=0 - 10.164.11.234 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 3:59:55 PM | 710014 | AnalogValue - 20 | present-value | Net=11001 - 4 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 3:59:55 PM | 710013 | AnalogValue - 6 | present-value | Net=11001 - 3 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 3:59:55 PM | 710014 | AnalogInput - 11 | present-value | Net=11001 - 4 - 47808 | Net=0 - 10.110.84.111 - 47808

## Slide 16
Excessive Events
-- Most recent 10
High Event traffic puts a burden on workstations or devices that must process each message. Try adjusting alarm limits or deadband values. These have more than 10 events in a minute.
Time | Source Instance | Object ID | Source Address | Destination Address
9/14/2020 4:05:55 PM | 4194282 | AnalogInput - 10155 | Net=0 - 10.167.6.27 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 4:01:55 PM | 30419 | EventEnrollment - 0 | Net=30400 - 19 - 47808 | Net=0 - 10.110.84.111 - 47808
9/14/2020 4:01:55 PM | 30419 | EventEnrollment - 4 | Net=30400 - 19 - 47808 | Net=0 - 10.110.84.111 - 47808

## Slide 17
High Broadcast Rate
-- Most recent 10
A high rate of broadcasts puts a burden on all devices that must processes the messages. Reduce COV broadcasts, remove failed node scans to non-existent devices, and fix failed devices to improve the health of the network. Those in this list had several of the same type in a minute.
Instance | Source Address | Destination Address | Service | Count
7300 | Net=0 - 10.240.58.231 - 47808 | 10.110.84.255 | IAmRouterToNetwork 730 | 19
70108 | Net=0 - 10.164.21.236 - 47808 | 10.110.84.255 | IAmRouterToNetwork 108 | 21
70308 | Net=0 - 10.160.25.51 - 47808 | 10.110.84.255 | IAmRouterToNetwork 8100, 8200, 8300 | 19
70123 | Net=0 - 10.161.8.109 - 47808 | 10.110.84.255 | IAmRouterToNetwork 10123 | 19
70303 | Net=0 - 10.160.32.64 - 47808 | 10.110.84.255 | IAmRouterToNetwork 30300 | 19
70202 | Net=0 - 10.161.24.229 - 47808 | 10.110.84.255 | IAmRouterToNetwork 2012, 2002 | 19
70203 | Net=0 - 10.167.6.230 - 47808 | 10.110.84.255 | IAmRouterToNetwork 65534, 55627, 55740, 55755, 55672, 55758, 55785, 55782, 5... | 19
70304 | Net=0 - 10.160.32.30 - 47808 | 10.110.84.255 | IAmRouterToNetwork 30400, 55734, 55737 | 19
70350 | Net=0 - 10.160.32.76 - 47808 | 10.110.84.255 | IAmRouterToNetwork 30200, 55795, 55769, 55730 | 18
70120 | Net=0 - 10.160.13.48 - 47808 | 10.110.84.255 | IAmRouterToNetwork 10120 | 19

## Slide 18
High Broadcast Rate Continued...
Instance | Source Address | Destination Address | Service | Count

## Slide 19
Incorrect Password Error
-- Most recent 10
A device has returned an invalid password error. Backups may not be happening until password is correct.
Time | Instance | Source Address | Destination Address | Count
9/14/2020 3:59:24 PM | 70101 | Net=0 - 10.161.52.31 - 47808 | Net=0 - 10.110.84.111 - 47808 | 112

## Slide 20
Overloaded/Restarting Device
-- Most recent 10
A Device may be overloaded or restarting. It was communicating, then failed to answer requests, but then does answer a failed node scan. A larger APDU timeout might help.
Time | Instance | Source Address | Count
9/14/2020 4:31:22 PM | 7162 | Net=7100 - 62 - 47808 | 1
9/14/2020 4:20:57 PM | 7161 | Net=7100 - 61 - 47808 | 2
9/14/2020 4:10:51 PM | 7160 | Net=7100 - 60 - 47808 | 6

## Slide 21
Preempted By Higher Priority Task
-- Most recent 10
A device usually returns this error code when it's overloaded or to busy to process a request. If it happens often it may not be functioning properly.
Time | Instance | Source Address | Destination Address | Count
9/14/2020 4:03:01 PM | (Unknown) | Net=0 - 10.160.32.75 - 47808 | Net=0 - 10.110.84.111 - 47808 | 11

## Slide 22
Reject Message to Network
-- Most recent 10
A router received a message it could not forward or a message that was not formatted correctly.
Time | Network | Reason | Count
9/14/2020 3:58:56 PM | 101 | Other | 2

## Slide 23
Timeout Error
-- Most recent 10
A device has returned a timeout error. It could be in a failed state, too busy to answer, or APDU timeout is too low.
Time | Instance | Source Address | Destination Address | Count
9/14/2020 4:08:46 PM | 70142 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.161.24.24 - 47808 | 5
9/14/2020 4:07:43 PM | 70144 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.160.25.47 - 47808 | 30
9/14/2020 4:07:37 PM | 70106 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.164.21.233 - 47808 | 10
9/14/2020 4:07:06 PM | 70125 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.164.21.21 - 47808 | 5
9/14/2020 4:06:53 PM | 70136 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.161.24.34 - 47808 | 5
9/14/2020 4:06:37 PM | 70135 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.161.24.68 - 47808 | 5
9/14/2020 4:06:32 PM | 70137 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.161.24.25 - 47808 | 145
9/14/2020 4:04:48 PM | 70309 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.160.25.37 - 47808 | 25
9/14/2020 4:04:34 PM | 9997 | Net=0 - 10.110.84.113 - 47808 | Net=0 - 10.160.25.30 - 47808 | 6
9/14/2020 4:04:28 PM | 70124 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.161.8.234 - 47808 | 6

## Slide 24
Unknown Object
-- Most recent 10
An unknown object error indicates an inconsistency problem between a field device and a workstation. For example, a write property might be trying to command an object that is not in the device.
Time | Reply Address | Request Address | Device Instance | Object ID | Property | Count
9/14/2020 4:12:54 PM | Net=0 - 10.161.8.234 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70124 | AnalogOutput - 11736 | priority-array | 1
9/14/2020 4:12:23 PM | Net=0 - 10.161.8.106 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70122 | AnalogInput - 13510 | status-flags | 1
9/14/2020 4:09:49 PM | Net=0 - 10.161.52.31 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70101 | TrendLog - 14 | log-device-object-property | 1
9/14/2020 4:07:17 PM | Net=0 - 10.161.24.26 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70143 | AnalogInput - 13109 | status-flags | 1
9/14/2020 4:03:58 PM | Net=0 - 10.161.8.109 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70123 | AnalogInput - 20109 | status-flags | 1
9/14/2020 4:02:17 PM | Net=0 - 10.161.24.25 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70137 | BinaryInput - 19478 | status-flags | 1
9/14/2020 3:59:28 PM | Net=35679 - 0.0.0.1.139.98 - 47808 | Net=0 - 10.110.84.111 - 47808 | 101218 | EventLog - 0 | log-device-object-property | 16
9/14/2020 3:59:17 PM | Net=0 - 10.160.25.34 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70305 | AnalogInput - 11803 | status-flags | 96
9/14/2020 3:59:07 PM | Net=0 - 10.160.32.64 - 47808 | Net=0 - 10.110.84.111 - 47808 | 70303 | AnalogInput - 0 | N/A | 192

## Slide 25
Unresponsive Device
-- Most recent 10
Unresponsive devices are those that do not answer a targeted who-is. They could be failed or they could be caused by misconfigured objects like notification classes. Those in this list have not answered at least 3 Who-Is requests.
Time | Instance | Source MAC Address
9/14/2020 4:08:22 PM | 2728781 | Net=0 - 10.161.24.229 - 47808
9/14/2020 4:07:18 PM | 2477603 | Net=0 - 10.161.8.234 - 47808
9/14/2020 4:06:04 PM | 2477821 | Net=0 - 10.160.25.27 - 47808
9/14/2020 4:05:01 PM | 2444086 | Net=0 - 10.161.52.31 - 47808
9/14/2020 4:04:30 PM | 2897632 | Net=0 - 10.160.25.25 - 47808
9/14/2020 4:04:26 PM | 80182 | Net=0 - 10.160.9.135 - 47808
9/14/2020 4:04:19 PM | 2655987 | Net=0 - 10.160.25.26 - 47808
9/14/2020 4:04:07 PM | 2743588 | Net=0 - 10.160.25.33 - 47808
9/14/2020 4:03:25 PM | 991006 | Net=0 - 10.161.8.108 - 47808
9/14/2020 4:02:50 PM | 2478719 | Net=0 - 10.167.6.230 - 47808

## Slide 26
Low Anomalies
Unanswered Request

## Slide 27
Unanswered Request
-- Most recent 10
A device that does not answer a request may be failed, overloaded, or have an APDU timeout that is too low. Devices in this list have one or more unanswered requests.
Time | Instance | Source Address | Destination Address | Count
9/14/2020 4:52:57 PM | 1010105 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 5 - 47808 | 1
9/14/2020 4:52:57 PM | 1010104 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 4 - 47808 | 1
9/14/2020 4:52:57 PM | 1010102 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 2 - 47808 | 2
9/14/2020 4:51:57 PM | 1010122 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 22 - 47808 | 1
9/14/2020 4:51:57 PM | 1010145 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 45 - 47808 | 1
9/14/2020 4:48:47 PM | 100 | Net=0 - 10.110.84.111 - 47808 | Net=0 - 10.167.6.78 - 47808 | 1
9/14/2020 4:17:56 PM | 7163 | Net=0 - 10.110.84.111 - 47808 | Net=7100 - 63 - 47808 | 3
9/14/2020 4:09:55 PM | 1010110 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 10 - 47808 | 2
9/14/2020 4:09:05 PM | 1010118 | Net=0 - 10.110.84.111 - 47808 | Net=101 - 18 - 47808 | 1
9/14/2020 4:08:55 PM | 8206 | Net=0 - 10.110.84.111 - 47808 | Net=8200 - 6 - 47808 | 8

## Slide 28
Top Traffic Counts

## Slide 29
Properties Generating COVs
-- Top 10
Device | Src Net | Src Addr | Dest Net | Dest Addr | Object Id | Property | Count
710014 | 11001 | 4 | 0 | 10.110.84.111 | AnalogValue - 20 | present-value | 3320
710013 | 11001 | 3 | 0 | 10.110.84.111 | AnalogValue - 6 | present-value | 3314
710014 | 11001 | 4 | 0 | 10.110.84.111 | AnalogInput - 11 | present-value | 2566
70104 | 0 | 10.164.11.234 | 0 | 10.110.84.111 | AnalogValue - 3 | present-value | 1802
70104 | 0 | 10.164.11.234 | 0 | 10.110.84.111 | AnalogInput - 1 | present-value | 1229
70121 | 0 | 10.161.8.108 | 0 | 10.110.84.111 | AnalogValue - 35 | present-value | 1207
710011 | 11001 | 1 | 0 | 10.110.84.111 | AnalogValue - 6 | present-value | 1096
710012 | 11001 | 2 | 0 | 10.110.84.111 | AnalogValue - 6 | present-value | 1012
70121 | 0 | 10.161.8.108 | 0 | 10.110.84.111 | AnalogValue - 34 | present-value | 857
70121 | 0 | 10.161.8.108 | 0 | 10.110.84.111 | AnalogValue - 33 | present-value | 669

## Slide 30
Objects Generating Events
-- Top 10
Device | Src Net | Src Addr | Dest Net | Dest Addr | Object Id | Count
30419 | 30400 | 19 | 0 | 10.110.84.111 | EventEnrollment - 4 | 234
4194282 | 0 | 10.167.6.27 | 0 | 10.110.84.111 | AnalogInput - 10155 | 198
30419 | 30400 | 19 | 0 | 10.110.84.111 | EventEnrollment - 0 | 178
70309 | 0 | 10.160.25.37 | 0 | 10.110.84.111 | TrendLog - 469 | 152
70309 | 0 | 10.160.25.37 | 0 | 10.110.84.111 | BinaryValue - 2 | 23
101218 | 0 | 10.160.27.98 | 0 | 10.110.84.111 | EventLog - 0 | 17
70122 | 0 | 10.161.8.106 | 0 | 10.110.84.111 | AnalogInput - 15 | 8
1010245 | 102 | 45 | 0 | 10.110.84.111 | EventEnrollment - 2 | 6

## Slide 31: Prioritized Summary
1 - Resolve Critical Anomalies
Critical
2 - Resolve High Anomalies
High
3 - Resolve Medium Anomalies
Med

## Slide 32: Network Anomaly Summary
Critical Anomaly Summary
Issue 1 Resolved by..
Issue 2 Resolved by..
Issue 3 Resolved by..
Issue 4 Resolved by..
Issue 5 Resolved by..
High Anomaly Summary
Issue 1 Resolved by..
Issue 2 Resolved by..
Issue 3 Resolved by..
Issue 4 Resolved by..
Issue 5 Resolved by..
Medium Anomaly Summary
Issue 1 Resolved by..
Issue 2 Resolved by..
Issue 3 Resolved by..
Issue 4 Resolved by..
Issue 5 Resolved by..

## Slide 33: Summary
BACPro monitors your network for over 40 different types of network problems and assigns a severity rating to them.
The data that has been captured and provided will help your building run more efficiently.
The summary section prioritizes network anomalies that need attention first.